## Slide 1
Become familiar with the Climatix libraries of functions including function and HVAC blocks, automation and BACnet objects.
Be able to develop own HVAC application programs
HVAC control
HVAC control

## Slide 2
Automation Objects overview
T
M
M
T
Hierarchy – Level 1
Pgm – Level 0
Type: Unit
aoHWIO
XT 1
XO 1
XT 2
XO 2
XT 3
XO 3
Type: Unit
aoHVAC
DO1
ID1
ID2
ID3
Controller HW
POL 6x8
XT 1
XO 1
XT 2
XO 2
DI 1
DO 1
DI 2
DO 2
DI 3
DO 3
X 10
DO 10
Description | Type | Signal | Unit | IO
Outside air temp. | AI | Ni1000 | °C | X1
Supply air temp. | AI | Ni1000 | °C | X2
Room air temp. | AI | Ni1000 | °C | X3
Fire alarm | DI | N/O Volt free cont. | Normal,ALARM | X4
Supply fan diff. pressure switch | DI | 24VAC signal | No Flow,Flow | D1
Extract fan diff. pressure switch | DI | 24VAC signal | No Flow,Flow | D2
Supply fan command | DO | 24V Relay | Off,On | Q1
Extract fan command | DO | 24V Relay | Off,On | Q2
Cooling coil valve | AO | 0-10V | % Open | X7
Heating coil valve | AO | 0-10V | % Open | X8
Temperature Control
Fan Control
Plant Control
HVAC control
T

## Slide 3
  Automation objects represent physical and software process values of a system within a controller (e.g. temperature, switch, actuator, setpoint etc) .
  Supported function types include:
      Binary input, output, value
      Analog input, output, value
      Multistate input, output, value
  Automation objects have internal functionality that can be configured.
  They make data available to clients (e.g. SCOPE, BACnet clients). Data is stored to flash memory during power off.
  In Climatix, most Automation objects are based on the BACnet standard.
SAPRO – Automation object library
Air handling unit (AHU)
Refrigeration machine (e.g chiller)
Automation Objects overview
– Automation objects
Of’
IN d’
IN e’
FB ‘Y’ - copy
RoomSetpoint
Type: FBD
1. Step no line only hardware
2. Step - line

## Slide 4
Automation Objects overview
– Automation objects

## Slide 5
Reliability
Present value
Sensor
Alarm handling
Value of low alarm
Value of high alarm
Stored in the Object storage
Value for high limit alarm
Value for low limit alarm
Limit range of the LimitLow and LimitHigh values
Engineering unit codes
Defines where and how the tracking value is determined
T
Modbus
Apl
COM
T
  Tracking (value) selector:
      Value direct from the application (default)
      Or from communications (e.g. Modbus)
  Apl Present value from the Application value COM Present value from the Communication value Average Present value is the average between Apl and COM Min Present value is the lower value of COM and Appl Max Present value is the higher value of COM and Appl PrfApl If Apl is good (Reliability ok), PrVAL is Apl, otherwise COM
  PrfCOM If COM is good (Reliability ok), PrVal is COM, otherwise Apl
  Binary input objects also have tracking selection with AND, OR options.
Analog input objects
– Automation objects
Device HWIO

## Slide 6
  Analog Output objects for damper and value actuators and Analog Value objects for process values.
  Both object types have priority array inputs.
  Analog output object has a tracking value reliability input, connected to the hardware IO if available on the device.
  Engineering units must be defined (e.g. percentage %).
  Both object types support alarming.
  Default member, value of PrVal when all values in the priority array have a NULL value.
Analog output and value objects
– Automation objects

## Slide 7
  Are used to monitor and control equipment with multiple conditions, e.g. unit mode switch (Off/On/Auto), 3 speed fan (stage 1, 2, 3).
  Multistate inputs, outputs and values
  An integer value represents a specific condition defined by the engineer, e.g. 1 = Off, 2 = On, 3 = Auto, 4 = Htg.
  Status text, the BACnet standard does not allow a state = 0, in SAPRO this is allowed therefore a NULL must be used.
SCOPE
SAPRO 0 1 2 3 4
Text Null Off On Auto Htg
BACnet 1 2 3 4
Status text: Null*Off*On*Auto*Htg
No. of states: 4
Multistate objects
– Automation objects

## Slide 8
Curser, mouse right button click.
Select <Automation Object (new)> to configured object.
Object type name
Instance name
Connectable inputs
Connectable outputs
SCOPE
  The Instance name must be unique in the application program.
  Display name used in clients like HMI and SCOPE. Default, the instance name is used, token is \i#
  Tval is the tracking value, i.e. the physical hardware input. PrVal is the present value.
  Many objects support intrinsic alarming that can be defined. The Status output is used for alarm functionality within the program. Disbl disables Offnormal alarms.
  In SAPRO, each object input, output and property is called a “Member”.
  Each member has a data format defined.
F1 – SAPRO help
Binary input objects
– Automation objects

## Slide 9
  Binary output objects (digital) are used to control switching outputs for fan and pumps.
  Tval is connected to a physical output, the value is determined by the priority array.
  Fback, if there is no real feedback, connect to Tval.
  StateText, must be defined with format Off*On*Null, change text as required.
Object type name
Instance name
Used for alarming
Tracking value
Alarm handling
Access to all members
Each input has a value and enable.
5 inputs are available on the object.
SCOPE
Automation Object(new) - options
Priority array – BACnet standard
Binary output objects
– Automation objects

## Slide 10
HW IO programming  Exercise 1
– HW IO programming
  For each Climatix device with physical inputs and outputs, an automation object is available. Example C600 controller.
  Function block for Climatix extension modules
POL688.10/STD controller
SAPRO project tree – xLib….
Hardware IO function block
Parameterized by selection the function block, right mouse click and select Automation Object(new).
Options for configuring the inputs and outputs

## Slide 11
  Universal PID controller (P, PI, PD, PID) with modulating output.
  Feedback signal input for the present control element position. If no real position feedback available, connect the analog output object PrVal to the AFBV input.
  Adjustable high and low limits for the output, Connect high and low inputs to the analog output object outputs.
  Connectable with further controllers to create sequences (SQ inputs and outputs).
SPV – set point value.
PRV – present value.
ERPRV – present value error.
ENBL – enable.
AO_UNA – control element unavailable.
AFBV – control element position feedback.
High – limit for the AO output.
Low – limit for the AO output.
INV – Invert control direction.
SQFM – sequence link (from more).
SQFL – sequence link (from less).
AO – output to analog output object.
Heating sequence
SPV
21 deg C
0 %
100 %
16 deg C
Proportional band 5 deg K
Output
KP =
max. output - min. output
proportional band (XP)
100% - 0%
5
100
5
=
20
=
=
Loop controller
– HVAC control functions

## Slide 12
  Sequence (SQxx) inputs and outputs to avoid multiple controllers operating simultaneously.
  If there is more than one controller in a sequence (e.g. heating and cooling), use the sequence in/outputs of the loop controller.
  Sequence inputs: Sequence outputs:
    SQFM – from more SQTM – to more
    SQFL – from less SQTL – to less
Loop controller  Exercise 2,3,4
– HVAC control functions
SQTM SQTL
Termination
Termination
SQTM
SQTL
SQFL
SQFM
SQTM
SQTL
SQFL
SQFM
SQTM
SQTL
SQFM
SQFL
Cooling sequence 1
Heating sequence 1
Heating sequence 2
Heating sequence 2
Cooling sequence 1
Heating demand
Cooling demand
KP +
KP -
Heating sequence 1
SQTL
SQTM
1
2
3
4

## Slide 13
  Used to determine the supply air temperature set point based on the room air temperature.
  Used in conjunction with a PID controller for the supply air controller control sequence.
SPVC - set point value cooling
SPVH - set point value heating
SPV – set point value (room air temp set point).
SPBAND – set point deadband.
SPSEL – set point selection.
PRV – Present value (room air temp).
ERPRV – Present value error.
ENBL – enable.
Cascade lead controller
– HVAC control functions

## Slide 14
  A Time Schedule can be used to:
    Switch on and off the Unit
    Switch Stages
    Change set points (analog Value)
    Do periodically pump running cycles
    …
  The time scheduler provides following features
    Define up to 6 switch events for each week day and one exception day
    Define up to 10 Calendar conditions for the exception day
Time Schedule  Exercise 5
– Time schedule
New recording
Just referring to the exercise not explaining the schematic in detail Delete that box when recording
Define Day Plan (Mon-Sun) + Exception
If the Date is active the exception days will be used