## Slide 1: University Training Docu-ments for SIMATIC PCS 7 Siemens Automation Cooperates with Education | 02/2020
siemens.com/sce
Unrestricted for Educational and R&D Institutions. © Siemens 2020. All Rights Reserved.

## Slide 2: Learn-/Training Documents PCS 7 Contents
  P01-01 Process description
  P01-02 Hardware configuration
  P01-03 Plant hierarchy
  P01-04 Individual drive functions
  P01-05 Functional safety
  P01-06 Control loop and other control functions
  P01-07 Importing plant design data
  P01-08 Sequential control systems
  P02-01 HMI generation
  P02-02 Alarm engineering
  P02-03 Archiving and trend reporting
MODULE 2
MODULE 1
Notes: 2

## Slide 3: Learn-/Training Documents PCS 7 Module 1 P01-01 Process description
  Classification of process plants
  P&ID of the laboratory plant
  Interlocks and recipes for the laboratory plant
Objectives
Notes: 3

## Slide 4: PCS Training Curriculums Module 1 P01-01 Process description
  Classification by the number of basically different products
    Single product process plant
    Multi-product process plant
  Classification according to the physical structure of the plant
    Single-train process plant
    Multi-train process plant
    Multi-train & multi-path process plant
  Laboratory plant as learning example
    Multi-product, multi-strand & multi-path plant
    Hierarchical breakdown into 4 plant units
Classification of process plants
Notes: 4

## Slide 5: Learn-/Training Documents PCS 7 Module 1 P01-01 Process description
Educt tanks
Reactors
Rinsing
Product tanks
P&ID of the laboratory plant
Notes: 5

## Slide 6: Learn-/Training Documents PCS 7 Module 1 P01-01 Process description
  Safe operation of the plant requires monitoring of process interventions
  Requirements for the laboratory plant:
    Control of actuators only when the main power switch is on and EMERGENCY OFF is unlocked
    Protection of the tanks against overflow
    Prevent the intake of air at the pumps
    Pumps must not work against closed valves
    …
  Production of a product requires a standard operating procedure
  Recipe for laboratory plant:
    350 ml of educt 3 to reactor 1 and 200 ml of educt 1 to reactor 2
    Heating of reactor 1 up to 25 °C and 150 ml of educt 2 to reactor 2
    …
Interlocks and recipes
Notes: 6

## Slide 7: Learn-/Training Documents PCS 7 Module 1 P01-02 Hardware configuration
  Theory
    Distributed structures
    Connection to the process
    Operating principle of a programmable logic controller (PLC)
  Step-by-step instruction
    Creating a project
    Configuring the hardware
    Configuring the communication
Objectives
Notes: 7

## Slide 8: Learn-/Training Documents PCS 7 Module 1 P01-02 Hardware configuration
  Special structures lead to scalable process control systems
  Structures are component based and can be easily expanded
  Typical structure:
    Process management level
    Control level
    Field level
Distributed structures of process control systems
Laboratory
Test center
Production plant
Connected facilities at one production site
SIMATIC PCS 7: 100 to 120 000 I/Os
SIMATIC PCS 7 LAB
Notes: 8

## Slide 9: Learn-/Training Documents PCS 7 Module 1 P01-02 Hardware configuration
  Two typical ways to connect sensors and actuators to the process control system
    Directly via a bus system (intelligent devices)
    To a signal module via a standard electrical signal
  Signal modules for
    Binary signals: DI/DO modules (DI .. digital input, DO .. digital output)
    1 bit of memory required per signal
    Analog signals: AI/AO modules (AI .. analog input, AO .. analog output)
    16 bits of memory required per signal
    Resolution can still be less, for example, 12 bits
Connection to the process
Notes: 9

## Slide 10: Learn-/Training Documents PCS 7 Module 1 P01-02 Hardware configuration
  Component on control level typically is a PLC
  Input and output signals are read and written cyclically and buffered in the process image
  Consistency of signals during program processing by accessing process image
Operating principle of the PLC
Initialization
Read the inputs
Write the outputs
Processing of operations of program blocks
Typical processing times:
1µs Bit operations 2µs Word operations
12µs Timer/counter operation 3µs Fixed-point addition
50µs Floating-point addition
Outputs
Process image outputs
Inputs
Process image inputs
Outputs
Process image outputs
Legend:
Access to hardware
Access to process image
Processing sequence
Notes: 10

## Slide 11: Learn-/Training Documents PCS 7 Module 1 P01-02 Hardware configuration
  AS
    PS
    CPU (with PROFIBUS)
      ET 200M (with PROFIBUS)
        7x DI
        3x DO
        1x AI
        1x AO
      CP (with Ethernet)
    OS
      PC (with Ethernet)
Hardware configuration of the laboratory plant
PC station as ES and OS with PCS 7 software and WinCC for visualization
Ethernet connection
S7 station as AS (here: CPU414-3DP)
ET 200M for I/O coupling
PROFIBUS DP
Notes: 11

## Slide 12: Learn-/Training Documents PCS 7 Module 1 P01-03 Plant hierarchy
  Theory
    Structuring the laboratory plant
    Deriving the visualization
    Plant hierarchy (PH) and structure of visualization
  Step-by-step instruction
    Opening the plant view
    Creating the plant hierarchy
    Basic settings of the plant hierarchy
Objectives
Notes: 12

## Slide 13: Learn-/Training Documents PCS 7 Module 1 P01-03 Plant hierarchy
  Structuring based on function aspect
  Hierarchical breakdown into units
    Unit 1: educt tanks
    Unit 2: reactors
    Unit 3: product tanks
    Unit 4: rinsing
  Design of an identification system according to ISA-88
    Process cell: A1
      Unit: T1 .. T4
        Equipment module: B001, …, B003, R001, …
        Control module: pump, valve, level, agitator, …
Structuring the laboratory plant
Notes: 13

## Slide 14: Learn-/Training Documents PCS 7 Module 1 P01-03 Plant hierarchy
  Deriving the visualization in the operator system (OS) through the following steps:
    Structuring the laboratory plant
    Creating the plant hierarchy
    Selection of a hierarchy level as OS area
    Running the generating process (see P02-01 HMI generation)
  All hierarchy levels below the level defined as OS area can be displayed automatically
    Area identification
    Navigation hierarchy
    Operating icons for implemented function blocks
    Group alarms
Deriving the visualization
Notes: 14

## Slide 15: Learn-/Training Documents PCS 7 Module 1 P01-03 Plant hierarchy
Plant hierarchy and the effect on visualization
OS area
Operating screens
A1_multipurpose plant
T2_reaction
Reactor R001
Reactor R002
T3_product tanks
Product tank B001
Product tank B002
T4_rinsing
Rinsing tank B001
T1_educt tanks
Educt tank B001
Educt tank B002
Educt tank B003
Notes: 15

## Slide 16: Learn-/Training Documents PCS 7 Module 1 P01-04 Individual drive functions
  Theory
    Terminology of individual drive functions (IDF)
    Individual drive functions in PCS 7
    Individual drive function Motor
  Step-by-step instruction
    Creating symbol tables
    Creating CFC for IDF Motor
    Testing the IDF
Objectives
Notes: 16

## Slide 17: Learn-/Training Documents PCS 7 Module 1 P01-04 Individual drive functions
  Hierarchical structuring of the plant according to DIN EN 61512
    Level 0: Control module
  Control module is a recurring element
    Project wide
    For more than one project
  Reusing possible
    Advantages:
    Parameterization instead of programming
    Tested functionality
    Consistent handling and visualization
  Type definition of control modules
    e. g. motor, valve, …
Individual drive functions (IDF)
Enterprise
Control module
may contain
may contain
may contain
must contain
Site
Area
Process cell
Unit
may contain
may contain
may contain
may contain
Equipment module
Notes: 17

## Slide 18: Learn-/Training Documents PCS 7 Module 1 P01-04 Individual drive functions
  Function blocks as object-oriented model of an equipment module
    e. g. motors and valves
  Functions:
    Control and control mode
    Protection and monitoring functions
    Operator control and visualization functions
    Messaging and alarm functions
  Function block as object-oriented model of a (measuring) signal
    e.g. digital output, digital input, analog output, analog input
  Functions:
    Scaling the digital value to the physical value range
    Monitoring the signal quality
Individual drive functions in PCS 7
Notes: 18

## Slide 19: Learn-/Training Documents PCS 7 Module 1 P01-04 Individual drive functions
  Function block MotL
  Used for controlling pumps/agitators in the laboratory plant
  Properties:
    Control with one control signal (on/off)
    Monitoring function through running feedback
  Advantages:
    No programming of the control, protection and monitoring functions
    Uniform parameters
    Uniform visualization (see P02-01 HMI generation)
Individual drive function MotL (PCS 7 Advanced Process Library)
Notes: 19

## Slide 20: Learn-/Training Documents PCS 7 Module 1 P01-04 Individual drive functions
  Pump SCE.A1.T2-P001 for draining the reactor content
  Pump is driven by a motor
  Motor has the following signals:
    Signal for control
    Signal for running feedback
  Template from PCS 7 AP library
    MotorLean
Implementation of a pump of the laboratory plant
Symbol | Address | Data type | Symbol comment
A1.T2.A1T2S003.SO+.O+ | I 1.3 | BOOL | pump outlet reactor R001 feedback on
A1.T2.A1T2S003.SV.C | Q 3.4 | BOOL | pump outlet reactor R001 actuating signal
Reactor
Notes: 20

## Slide 21: Learn-/Training Documents PCS 7 Module 1 P01-05 Functional safety
  Theory
    Functional safety with tools of process control engineering (PCE)
    Standard circuits for functional safety
    Design of an interlock for the laboratory plant
  Step-by-step instruction
    Creating CFC for manual operation of the motor
    Adding the interlock for motor in CFC
    Interconnections between CFCs
Objectives
Notes: 21

## Slide 22: Learn-/Training Documents PCS 7 Module 1 P01-05 Functional safety
  Protection of process plants against fault states
  In reference to the process variables, there are 3 value ranges
Functional safety with tools of process control engineering (PCE)
Curve 1
Curve 2
Curve 3
Limit value of protective equipment
Limit value of monitoring device
time
process value
Intended use
Acceptance region
Permissible deviation
Non-permissible deviation
Non-intended use
Non-PCE protective device responds
Event-preventing PCE protective responds
PCE monitoring device responds
Process-related limit value
Notes: 22

## Slide 23: Learn-/Training Documents PCS 7 Module 1 P01-05 Functional safety
  The pump may only be turned on when the main switch of the plant is switched on and the Emergency Off switch is unlocked
  The pump must not take in air, which means the level of the reactor has to be at least 50 ml
  The pump must not work against closed valves, which means at least one valve has to be open
Design of the interlock for the pump of the laboratory plant
Symbol | Address | Data type | Symbol comment
A1.A1H001.HS+-.START | I 0.0 | BOOL | Switch on main power switch
A1.A1H002.HS+-.OFF | I 0.1 | BOOL | Activate EMERGENCY OFF
A1.T2.A1T2L001.LISA+.M | IW 72 | WORD | Actual value level reactor R001
A1.T2.A1T2X007.GO+-.O+ | I 66.3 | BOOL | Open/Closed valve … feedback signal
A1.T3.A1T3X001.GO+-.O+ | I 67.4 | BOOL | Open/Closed valve … feedback signal
A1.T4.A1T4X003.GO+-.O+ | I 68.2 | BOOL | Open/Closed valve … feedback signal
Notes: 23

## Slide 24: Learn-/Training Documents PCS 7 Module 1 P01-05 Functional safety
  Replacement of analog value A1.T2.A1T2L001.LISA+.M by a binary value that is the result of the comparison with 50 ml
  Function table for design of combinatorial circuit
  Result according to conjunctive normal form (CNF) is used for the interlock of the pump
Standard circuits for functional safety
A1T2L001 > 50ml | A1T2X007 | A1T3X001 | A1T4X003 | LOCK
x | x | x | x | 0
x | x | x | x | 0
0 | x | x | x | 0
x | 0 | 0 | 0 | 0
1 | 1 | x | x | 1
1 | x | 1 | x | 1
1 | x | x | 1 | 1
Notes: 24

## Slide 25: Learn-/Training Documents PCS 7 Module 1 P01-06 Control loop and other control functions
  Theory
    Structure of a control loop
    PID controller
    Temperature control of the laboratory plant
  Step-by-step instruction
    Parameterization of a continuous controller
    Output of the analog manipulated variable as a binary signal with a pulse generator
Objectives
Notes: 25

## Slide 26: Learn-/Training Documents PCS 7 Module 1 P01-06 Control loop and other control functions
  Process variables have to keep or achieve certain values
    Disturbance behavior: A certain value has to be kept in spite of disturbances
    Response to setpoint changes: Setpoint shall be achieved in a dynamic and stable manner
  Control loop works as follows:
    Process variable or controlled variable is measured by a sensor
    Setpoint minus measured value equals the system deviation
    Controller calculates a value of the manipulated variable for the actuator on the basis of the deviation
    Actuator acts on the system
Structure of a control loop
Loop controller
System
Disturbance variables z
Manipulated variable y
Process variable = controlled variable x
(System) deviation e
Setpoint w
+
-
Notes: 26

## Slide 27: Learn-/Training Documents PCS 7 Module 1 P01-06 Control loop and other control functions
  Control algorithm calculates the value of the manipulated variable from the deviation
  Process industry uses the PID algorithm to 95%
    P stands for proportional
      Current manipulated variable value depends only on the current deviation
    I stands for integral
      Current manipulated variable value depends on the sum of the last deviations
    D stands for differential
      Current manipulated variable value depends on the change of the deviation
  Only three parameters (gain, integral-action time and derivative-action time) have to be adjusted
  Practical tuning rules exist for processes without dominant dead times
    Ziegler and Nichols method
    Chien, Hrones and Reswick
PID controller
Notes: 27

## Slide 28: Learn-/Training Documents PCS 7 Module 1 P01-06 Control loop and other control functions
Temperature control of the laboratory process cell
  Control loop
    Process variable/controlled variable is A1.T2.A1T2T001.TIC.M
    Manipulated variable is A1.T2.A1T2T001.TV.S
    Setpoint is
      Determined by recipe
      Determined by operator
      Interlocked
  Interlock conditions
    Level in the reactor has to be at least 200 ml
    Temperature must not exceed 60 °C
Notes: 28

## Slide 29: Learn-/Training Documents PCS 7 Module 1 P01-07 Importing plant design data
  Theory
    Design of complex systems
    Process tag type
    Model
  Step-by-step instruction
    Importing plant design data using the Import/Export Assistant
    Importing plant design data in the process object view
    Duplicating charts by creating process tag types/models
Objectives
Notes: 29

## Slide 30: Learn-/Training Documents PCS 7 Module 1 P01-07 Importing plant design data
  Three general design principles
    Principle of hierarchical arrangement
      Plant hierarchy
    Principle of modularization
      Scope and complexity of blocks, CFC and SFC
    Principle of reuse
      Process tag types and models
  Reuse also implies
    Use of proven solutions (standards)
    Central modifiability
    Tested implementation
Design of complex systems
Notes: 30

## Slide 31: Learn-/Training Documents PCS 7 Module 1 P01-07 Importing plant design data
  Process tag type (CFC) – corresponds to control module level
  Model (entire hierarchy) – corresponds to equipment module or unit level
Process tag types and models
Level
Physical model
Interlock
Alarm management
Control module
Equipment module
Unit
Process cell
very individual
types can be created
copying possible
for the most part
Notes: 31

## Slide 32: Learn-/Training Documents PCS 7 Module 1 P01-07 Importing plant design data
  Selecting similar control modules
    Pumps
      A1T1P001, A1T1P002, A1T1P003 and A1T4P001
      A1T2P001 and A1T2P002
    Valves
      A1T1V001, A1T1V002, A1T1V003, .. , A1T1V006
      ...
  Selecting similar equipment modules
    Tanks
      A1T1B001, A1T1B002 and A1T1B003
      A1T2R001 and A1T2R002
      A1T3B001 and A1T3B002
Process tag type and model of the laboratory plant
Notes: 32

## Slide 33: Learn-/Training Documents PCS 7 Module 1 P01-08 Sequential control systems
  Theory
    Structure of sequential function charts
    Design of a sequential control system
    Recipe of the laboratory plant
  Step-by-step instruction
    Creating and editing a sequential function chart (SFC)
    Linking of SFC and CFC
    Testing the SFC
Objective
Notes: 33

## Slide 34: Learn-/Training Documents PCS 7 Module 1 P01-08 Sequential control systems
  Alternating sequence of steps and transitions
    First step: initial step
    Lasat step: final step
  Structures:
    Unbranched sequential function chart
    Alternative branches
    Parallel branches
  Illegal structures:
    Uncertain sequence – accessibility not assured
    Partial deadlock – internal infinite loop
    Total deadlock – no permissible step enabling condition
  One time or cyclical processing of sequential function chart is possible
Structure of sequential function charts
Notes: 34

## Slide 35: Learn-/Training Documents PCS 7 Module 1 P01-08 Sequential control systems
  Proven design method for sequential control systems
    State diagrams
      Connected and directed graph
      States shown as circles – can be linked with actions
      State transitions shown as arrows – can be subject to transition conditions
    Petri nets
      Consists of locations and transitions
      Locations shown as circles
      Transitions shown as rectangles/bars
      Parallel sequences can be displayed
Design of a sequential control system
Notes: 35

## Slide 36: Learn-/Training Documents PCS 7 Module 1 P01-08 Sequential control systems
  First, 350 ml are to be drained from educt tank A1.T1.B003 into reactor A1.T2.R001 and at the same time 200 ml from educt tank A1.T1.B002 into reactor A1.T2.R002.
  When reactor A1.T2.R001 is filled, the liquid is to be heated to 25 °C with the agitator switched on.
  When filling of reactor A1.T2.R002 is finished, 150 ml from educt tank A1.T1.B001 is to be added to reactor A1.T2.R002. When this is finished, the agitator of reactor A1.T2.R002 is to be switched on 10 s later.
  When the temperature of the liquid in reactor A1.T2.R001 has reached 25 °C, the mixture is to be pumped from reactor A1.T2.R002 to reactor A1.T2.R001.
  Now, the mixture in reactor A1.T2.R001 is to be heated to 28 °C and then drained into product tank A1.T3.B001.
Recipe of the laboratory plant
Notes: 36

## Slide 37: Learn-/Training Documents PCS 7 Module 2 P02-01 HMI generation
  Theory
    Concepts of representation
    HMI generation in PCS 7
    Graphics of the laboratory plant
  Step-by-step instruction
    Generating the operator station (OS) in SIMATIC Manager
    Configuration environment WinCC
    Creating pictures with the Graphics Designer
Objectives
Notes: 37

## Slide 38: Learn-/Training Documents PCS 7 Module 2 P02-01 HMI generation
  Important aspects of representation
    Organization of what is to be represented
    Degree of filling
    Coding
    Conspicuousness
    Consistency
  Basic structure of display area according to VDI 3699
  Flowcharts
    Process control flowcharts
    Process flowcharts
      Basic flowchart, process flowchart, P&ID flowchart
Concepts of representation
Message line
Overview area
Key area
Window
Working area
Notes: 38

## Slide 39: Learn-/Training Documents PCS 7 Module 2 P02-01 HMI generation
  Picture hierarchy can be derived directly from plant hierarchy
    Creating a picture in the corresponding levels
  Using the block icons of templates
    Deriving block icons from the plant hierarchy
  Configuring different OS areas
    For example, unit T1 is monitored by operator 1, T2 to T4 by operator 2
  Monitor configuration
    Representation for different resolutions, numbers and arrangement of monitors
  Graphics Designer
    Drawing the process pictures (static elements)
    Linking dynamic elements with the process tags
HMI generation in PCS 7
Notes: 39

## Slide 40: Learn-/Training Documents PCS 7 Module 2 P02-01 HMI generation
  Hierarchy includes level 1 and 2
  Overview screen
    Displays all units
    Displays the most important information
    Abstract
  Area display
    Display of a unit
    Display of faceplate icons of motors and valves
    Display resembling the P&ID
Graphics of the laboratory plant
Notes: 40

## Slide 41: Learn-/Training Documents PCS 7 Module 2 P02-02 Alarm engineering
  Theory
    Message systems
    Alarms and messages
    Alarm management in PCS 7
  Step-by-step instruction
    Integration of monitoring and alarm blocks
    Message system of WinCC
    Display of alarms and warnings in the operator station (OS)
Objectives
Notes: 41

## Slide 42: Learn-/Training Documents PCS 7 Module 2 P02-02 Alarm engineering
  Interface between process and operator
    Early detection of deviations from the desired state
    Specific interventions to restore the desired state
  Alarm display or report of occurrence of an event that requires immediate action of the operator
  Message display or report of occurrence of an event that requires no immediate action of the operator
  Properties for selection of alarms
    Relevant
    Unambiguous
    Timely
    Prioritized
    Comprehensible
Message system, alarms and messages
Response time | Potential effect |  | 
 | Plant shutdown | Loss of production | Delay in production
< 5 min | High | Medium | Low
5 - 20 min | Medium | Low | Low
> 20 min | Low | Low | Low
Priority
Priority
Notes: 42

## Slide 43: Learn-/Training Documents PCS 7 Module 2 P02-02 Alarm engineering
  Function block for generating messages
    Block icons for display of alarm states
  Group alarms along the plant hierarchy
  Display and management of message lists
Alarm management in PCS 7
Notes: 43

## Slide 44: Learn-/Training Documents PCS 7 Module 2 P02-02 Alarm engineering
  Monitoring of level
  Monitoring of temperature
  Using MonAnS block (FB 1912) from Monitor folder of the PCS 7 Advanced Process Library V80
    Monitoring a measured value (analog signal)
    Adjustable parameters
      Warning limit (high/low)
      Alarm limit (high/low)
  Display of faceplate icon
    In unit T2_reaction
    Positioning and compiling
Alarms for the laboratory plant
Notes: 44
To Do

## Slide 45: Learn-/Training Documents PCS 7 Module 2 P02-03 Archiving and trend reporting
  Theory
    Goals of archiving
    Archiving on the OS server
    Short-term and long-term archiving
    Trend reporting
  Step-by-step instruction
    Activating archiving in CFC
    Archive settings of the OS server
    Trend groups and reports
Objectives
Notes: 45

## Slide 46: Learn-/Training Documents PCS 7 Module 2 P02-03 Archiving and trend reporting
  Why must process data and events be saved?
    Legal requirements: logging of faults, verification for compliance with requirements, gapless tracking of the production cycle for product liability purposes
    Process management: statistics of production data, optimization of production, increasing of performance, optimization of material and manufacturing costs
    Safety: analysis of production data for adapting production parameters, in particular limits and response times, verification of functional safety when testing interlocks and EMERGENCY OFF functions
    Performance: increasing of performance of the process database, data backup
Goals of archiving
Notes: 46

## Slide 47: Learn-/Training Documents PCS 7 Module 2 P02-03 Archiving and trend reporting
  Archiving on the OS server = short-term archiving
    Process values
      Slow cycle Tag logging slow
      Fast cycle Tag logging fast
    Messages/events Alarm logging
  Structure of the archives (Tag logging slow/fast, Alarm logging)
    Circular archive consisting of segments
Archiving on the OS server
full segments
current segment
30 bytes/value
max. 30 bytes/value
200 to 400 bytes/message
Memory on the OS serve
Notes: 47

## Slide 48: Learn-/Training Documents PCS 7 Module 2 P02-03 Archiving and trend reporting
  Short-term archiving on the OS servers
  Long-term archiving on a Central Archive Server
  Process values archive slow archive fast
  Messages/events message archive
  Charge reports, OS reports report archive
  Central Archive Server (CAS) gathers data for long-term archiving from multiple OS servers and Batch servers
  CAS can be configured redundantly for increased data security
  CAS has no connection to the automation system
Short-term and long-term archiving
OS server (redundant)
Batch server (redundant)
Central Archive Server (CAS)
Automation systems
Terminal bus
Plant bus
OS clients
Notes: 48

## Slide 49: Learn-/Training Documents PCS 7 Module 2 P02-03 Archiving and trend reporting
  Trend reporting = Representation of process values in curves (i.e. graphical representation of process values over time)
  Possible representations in PCS 7
    Trend groups
    Online Trend Control
    Online Function Control (deviates from the definition of trends but displays process values depending on other process values)
  Representation of archive tags by accessing the archives on the OS server
  Representation of online tags by buffering the current process values
    Useful for process values that are not archived
    Buffering only as long as the display is shown
Trend reporting
Notes: 49

## Slide 50: Learn-/Training Documents PCS 7 Benefits
Theoretical and practical introduction to process control engineering of a process plant – in general and with PCS 7 at the university level
Guided implementation based on available projects or implementation of your own designs possible
Testing the implementation in a simulated plant

## Slide 51: Learn-/Training Documents PCS 7 Outlook
  As a lecture (= theory) with practice (= exercises) to design a solution and to implement the design in PCS 7
  As practical training (= exercises) to design a solution and to implement the design in PCS 7
or
  As self-study to implement projects with PCS 7
Use of the documents in training/education

## Slide 52: Thank you for your attention!
Siemens Automation Cooperates with Education
Subject to changes and errors. The information given in this document only contains general descriptions and/or performance features which may not always specifically reflect those described, or which may undergo modification in the course of further development of the products. The requested performance features are binding only when they are expressly agreed upon in the concluded contract.
All product designations, product names, etc. may contain trademarks or other rights of Siemens, its affiliated companies or third parties. Their unauthorized use may infringe on the rights of the respective owner.
siemens.com/sce